## PacketFormat
| Update Rate (Hz) | 5
Scaling
Header | Name | DataType | Points | Qty | Total B/s | Gain | Units - Notes
| Start byte | int16 | 1 | 1 | 10 |  | 0xAFAF
Waveform Data | Waveform | int16 | 1 | 3 | 30 | 1 | Vpu
Relay Data | Power Real | int16 | 1 | 59 | 590 | 10 | kw
Relay Data | Power Reactive | int16 | 1 | 59 | 590 | 10 | kvar
Relay Data | Voltage | int16 | 1 | 59 | 590 | 100 | Vpu
Relay Data | Frequency | int16 | 1 | 59 | 590 | 100 | Hz
Relay Data | Breaker Status | int16 | 1 | 59 | 590 | 1 | may change to Bit field - 8bits per breaker
BESS Data | Battery SoC [%] | int16 | 1 | 1 | 10 | 100 | N/A
BESS Data | Voltage | int16 | 1 | 1 | 10 | 100 | VRMSLL
BESS Data | Frequency | int16 | 1 | 1 | 10 | 100 | Hz
BESS Data | Power Real | int16 | 1 | 1 | 10 | 100 | kW
BESS Data | Power Reactive | int16 | 1 | 1 | 10 | 100 | kVAR
Diesel Gensets data | Terminal voltage diesel | int16 | 1 | 1 | 10 | 100 | Vpu
Diesel Gensets data | Fuel comsumption | int16 | 1 | 1 | 10 | 100 | gals/hr
NGCHP Gensets data | Terminal voltage NGCHP | int16 | 1 | 1 | 10 | 100 | Vpu
NGCHP Gensets data | Temp Actual | int16 | 1 | 1 | 10 | 100 | degrees C
NGCHP Gensets data | Heat Recovered | int16 | 1 | 1 | 10 | 100 | Mbtu/hr
NGCHP Gensets data | Fuel usage | int16 | 1 | 1 | 10 | 100 | Nm^3/hr
NGCHP Gensets data | CHP CO2 | int16 | 1 | 1 | 10 | 100 | lbm/hr
NGCHP Gensets data | Heat from boiler | int16 | 1 | 1 | 10 | 100 | Mbtu/hr
NGCHP Gensets data | CHP heat contribution | int16 | 1 | 1 | 10 | 100 | Mbtu/hr
NGCHP Gensets data | Boiler Nm^3/hr | int16 | 1 | 1 | 10 | 100 | Nm^3/hr
NGCHP Gensets data | Boiler lbm/hr CO2 | int16 | 1 | 1 | 10 | 100 | lbm/hr
Motor data | F3 Motor Status | int16 | 1 | 1 | 10 | 1 | on/off state
Motor data | F1 Motor Status | int16 | 1 | 1 | 10 | 1 | on/off state
PV data | Voltage | int16 | 1 | 1 | 10 | 100 | VRMSLL
PV data | Power Real | int16 | 1 | 1 | 10 | 100 | kW
PV data | Power Reactive | int16 | 1 | 1 | 10 | 100 | kVAR
Power Factor Data | Power Factor | int16 | 1 | 3 | 30 | 1000 | N/A
Power Factor Data | Import/Export | int16 | 1 | 3 | 30 | 1 | 1:import/0:export
Power Factor Data | Lagging/Leading | int16 | 1 | 3 | 30 | 1 | 1:lagging/0:leading
Misc Data - 1 | Load Real Power | int16 | 1 | 25 | 250 | 1 | kW
Misc Data - 1 | Load Voltage | int16 | 1 | 25 | 250 | 1 | VRMSLL
Misc Data - 2 | DMS - Disconnect request | int16 | 1 | 1 | 10 | 100 | LO: No active, HI: Active
Misc Data - 2 | DMS - kW import request - Value | int16 | 1 | 1 | 10 | 100 | kW
Misc Data - 2 | DMS - kW import request - Enable | int16 | 1 | 1 | 10 | 100 | LO: No active, HI: Active
Misc Data - 2 | DMS - PF Correction - Value | int16 | 1 | 1 | 10 | 100 | N/A
Misc Data - 2 | DMS - PF Correction - Enable | int16 | 1 | 1 | 10 | 100 | LO: No active, HI: Active
Misc Data - 2 | DMS - kW export request - Value | int16 | 1 | 1 | 10 | 100 | kW
Misc Data - 2 | DMS - kW export request - Enable | int16 | 1 | 1 | 10 | 100 | LO: No active, HI: Active
Misc Data - 2 | Auto-synchronize - Enable | int16 | 1 | 1 | 10 | 100 | LO: No active, HI: Active
Misc Data - 2 | Microgrid controller start - Enable | int16 | 1 | 1 | 10 | 100 | LO: No active, HI: Active
Misc Data - 2 | Blackstart - Enable | int16 | 1 | 1 | 10 | 100 | LO: No active, HI: Active
Misc Data - 3 | Test Sequence - Fault 1 | int16 | 1 | 1 | 10 | 100 | LO: No active, HI: Active
Misc Data - 3 | Test Sequence - Fault 2 | int16 | 1 | 1 | 10 | 100 | LO: No active, HI: Active
Misc Data - 3 | Test Sequence - Fault 3 | int16 | 1 | 1 | 10 | 100 | LO: No active, HI: Active
Misc Data - 3 | Test Sequence - Fault 4 | int16 | 1 | 1 | 10 | 100 | LO: No active, HI: Active
Misc Data - 3 | Test Sequence - Fault 5 | int16 | 1 | 1 | 10 | 100 | LO: No active, HI: Active
Misc Data - 3 | Test Sequence - Loss of upstream | int16 | 1 | 1 | 10 | 100 | LO: No active, HI: Active
Misc Data - 3 | Test Sequence - Irradiance | int16 | 1 | 1 | 10 | 100 | W/m^3
Misc Data - 3 | Test Sequence - Motor 1 On/Off | int16 | 1 | 1 | 10 | 100 | LO: No active, HI: Active
Misc Data - 3 | Test Sequence - Motor 2 On/Off | int16 | 1 | 1 | 10 | 100 | LO: No active, HI: Active
| Stop byte | int16 | 1 | 1 | 10 |  | 0x5555
| Checksum | int16 | 1 | 1 | 10 |  | Add all the bytes with overflow. Send bottom 16-bits
400
|  |  |  | Total Data Rate (B/s) | 4000

## Relay Data - Order
Device | IP Address | TCP Port | Feeder Location ID | Notes
Generic Relay CB301 | 192.168.10.133 | 502 | F3 | -
Generic Relay CB302 | 192.168.10.134 | 502 | F3 | -
Generic Relay CB303 | 192.168.10.135 | 502 | F3 | MCB for Natural Gas/CHP
Generic Relay CB304 | 192.168.10.136 | 502 | F3 | -
Generic Relay CB305 | 192.168.10.137 | 502 | F3 | -
Generic Relay CB306 | 192.168.10.138 | 502 | F3 | -
Generic Relay CB307 | 192.168.10.139 | 502 | F3 | Controls CB for Priority Load P4
Generic Relay CB308 | 192.168.10.140 | 502 | F3 | Controls CB for Interruptible Load I6
Generic Relay CB309 | 192.168.10.141 | 502 | F3 | Controls CB for Priority Load P6
Generic Relay CB201 | 192.168.10.115 | 502 | F2 | -
Generic Relay CB202 | 192.168.10.116 | 502 | F2 | -
Generic Relay CB203 | 192.168.10.117 | 502 | F2 | -
Generic Relay CB204 | 192.168.10.118 | 502 | F2 | Controls CB for Priority Load P3
Generic Relay CB205 | 192.168.10.119 | 502 | F2 | Controls CB at BESS (EPC)
Generic Relay CB206 | 192.168.10.120 | 502 | F2 | Controls CB for Interruptible Load I3
Generic Relay CB207 | 192.168.10.121 | 502 | F2 | -
Generic Relay CB208 | 192.168.10.122 | 502 | F2 | Controls CB for Interruptible Load I4
Generic Relay CB209 | 192.168.10.123 | 502 | F2 | -
Generic Relay CB210 | 192.168.10.124 | 502 | F2 | -
Generic Relay CB211 | 192.168.10.125 | 502 | F2 | Controls CB at PV (EPC)
Generic Relay CB212 | 192.168.10.126 | 502 | F2 | Controls CB for Interruptible Load I5
Generic Relay CB213 | 192.168.10.127 | 502 | F2 | Controls tie: F2 and F3 at 480 V
Generic Relay CB214 | 192.168.10.128 | 502 | F2 | -
Generic Relay CB215 | 192.168.10.129 | 502 | F2 | -
Generic Relay CB216 | 192.168.10.130 | 502 | F2 | Controls tie: F2 and F3 at 480 V
Generic Relay CB217 | 192.168.10.130 | 502 | F2 | Controls tie: F2 and F3 at 480 V
Generic Relay CB218 | 192.168.10.131 | 502 | F2 | Controls CB for Priority Load P5
Generic Relay CB219 | 192.168.10.132 | 502 | F2 | Controls CB for Priority Load P2
Generic Relay CB101 | 192.168.10.101 | 502 | F1 | -
Generic Relay CB102 | 192.168.10.102 | 502 | F1 | -
Generic Relay CB103 | 192.168.10.103 | 502 | F1 | MCB for Diesel Genset
Generic Relay CB104 | 192.168.10.104 | 502 | F1 | Controls CB for Interruptible Load I1
Generic Relay CB105 | 192.168.10.105 | 502 | F1 | -
Generic Relay CB106 | 192.168.10.106 | 502 | F1 | -
Generic Relay CB107 | 192.168.10.107 | 502 | F1 | Controls CB for Interruptible Load I2
Generic Relay CB108 | 192.168.10.108 | 502 | F1 | Controls tie: F1 and F2 at 13.8 kV
Generic Relay CB109 | 192.168.10.109 | 502 | F1 | Controls tie: F1 and F2 at 480 V
Generic Relay CB110 | 192.168.10.110 | 502 | F1 | -
Generic Relay CB111 | 192.168.10.111 | 502 | F1 | Controls tie: F1 and F2 at 4.16 kV
Generic Relay CB112 | 192.168.10.112 | 502 | F1 | -
Generic Relay CB113 | 192.168.10.113 | 502 | F1 | Controls tie: F1 and F3 at 480 V
Generic Relay CB114 | 192.168.10.114 | 502 | F1 | CB for Priority Load P1, same bus as motor load
SEL-751 Relay 3 | 192.168.10.53 | 502 | F3 | F3 POI interconnection relay
SEL-751 Relay 2 | 192.168.10.52 | 502 | F2 | F2 POI interconnection relay
SEL-751 Relay 1 | 192.168.10.51 | 502 | F1 | F1 POI interconnection relay
Natural Gas GCB | N/A | N/A | F3 | Woodward EasyGen 3500 controlling the 3.5 MVA natural gas-fired combined heat and power system
Diesel Genset GCB | N/A | N/A | F1 | Woodward EasyGen 3500 controlling the 4 MVA diesel genset
BESS_MX1 | N/A | N/A | F2 | Relay located after the BESS filter and controlled by the EPC board

## MiscData1 - Order
Load | Attribute | Scale Factor
I1 | kW | 100
I2 | kW | 100
I3 | kW | 100
I4 | kW | 100
I5 | kW | 100
I6 | kW | 100
P1 | kW | 100
P2 | kW | 100
P3 | kW | 100
P4 | kW | 100
P5 | kW | 100
P6 | kW | 100
C1 | kW | 100
C2 | kW | 100
C3 | kW | 100
C4 | kW | 100
C5 | kW | 100
C6 | kW | 100
I1 | VRMSLL | 100
I2 | VRMSLL | 100
I3 | VRMSLL | 100
I4 | VRMSLL | 100
I5 | VRMSLL | 100
I6 | VRMSLL | 100
P1 | VRMSLL | 100
P2 | VRMSLL | 100
P3 | VRMSLL | 100
P4 | VRMSLL | 100
P5 | VRMSLL | 100
P6 | VRMSLL | 100
C1 | VRMSLL | 100
C2 | VRMSLL | 100
C3 | VRMSLL | 100
C4 | VRMSLL | 100
C5 | VRMSLL | 100
C6 | VRMSLL | 100